## Map
Analog Channels |  | 2024-10-07 |  | TR24-0131 / 450 Ton | WC 500-3 SR
Ref ID | DAQ Driver | Channel | Serial number | Description/Location | LabVIEW Tag Names | Range
P1 | %DAQ3B_AI_001% | DAQ3B: mA: 1 | 460456 | COMPRESSOR SUCTION PRESSURE | COMPR_SYS01_RVAP_SUCT_PRESS_01 | 0-250 psia
P2 | %DAQ3B_AI_002% | DAQ3B: mA: 2 | 481329 | COMRPRESSOR DISCHARGE PRESSURE | COMPR_SYS01_RVAP_DISCH_PRESS_01 | 0-250 psia
P3 | %DAQ3B_AI_003% | DAQ3B: mA: 3 | 460452 | CONDENSER PRESSURE | COND_SYS01_RVAP_HIGH-CTR_PRESS_01 | 0-250 psia
P4 | %DAQ3B_AI_004% | DAQ3B: mA: 4 | 481330 | OIL PRESSURE | OIL_SYS01_OIL_PUMP_PRESS_01 | 0-250 psia
P5 | %DAQ3B_AI_005% | DAQ3B: mA: 5 | 446104 | OIL SUMP PRESSURE | OIL_SYS01_OIL_SUMP-MID_PRESS_01 | 0-250 psia
P6 | %DAQ3B_AI_006% | DAQ3B: mA: 6 | 489945 | BAROMETRIC PRESSURE | AMB_UNIT_AIR_EXT_PRESS_01 | 0-50 psia
DP1 | %DAQ3B_AI_007% | DAQ3B: mA: 7 | 1505060 | EVAPORATOR WATER PRESSURE DROP | EVAP_UNIT_WTR_NOZ_DP_01 | 0-45 ft,H2O
DP2 | %DAQ3B_AI_008% | DAQ3B: mA: 8 | 1142262 | CONDENSOR WATER PRESSURE DROP | COND_UNIT_WTR_NOZ_DP_01 | 0-45 ft,H2O
DP3 | %DAQ3B_AI_009% | DAQ3B: mA: 9 | 1043692 | OIL COOLER WATER PRESSURE DROP | OIL_UNIT_WTR_NOZ_DP_01 | 0-45 ft,H2O
| %DAQ3B_AI_010% | DAQ3B: mA: 10
| %DAQ3B_AI_011% | DAQ3B: mA: 11
| %DAQ3B_AI_012% | DAQ3B: mA: 12
| %DAQ3B_AI_013% | DAQ3B: mA: 13
| %DAQ3B_AI_014% | DAQ3B: mA: 14
| %DAQ3B_AI_015% | DAQ3B: mA: 15
| %DAQ3B_AI_016% | DAQ3B: mA: 16
| %DAQ3B_AI_017% | DAQ3B: mA: 17
| %DAQ3B_AI_018% | DAQ3B: mA: 18
| %DAQ3B_AI_019% | DAQ3B: mA: 19
| %DAQ3B_AI_020% | DAQ3B: mA: 20
| %DAQ3B_AI_021% | DAQ3B: mA: 21
| %DAQ3B_AI_022% | DAQ3B: mA: 22
| %DAQ3B_AI_023% | DAQ3B: mA: 23
| %DAQ3B_AI_024% | DAQ3B: mA: 24
| %DAQ3B_AI_025% | DAQ3B: mA: 25
| %DAQ3B_AI_026% | DAQ3B: mA: 26
| %DAQ3B_AI_027% | DAQ3B: mA: 27
| %DAQ3B_AI_028% | DAQ3B: mA: 28
| %DAQ3B_AI_029% | DAQ3B: mA: 29
| %DAQ3B_AI_030% | DAQ3B: mA: 30
| %DAQ3B_AI_031% | DAQ3B: mA: 31
| %DAQ3B_AI_032% | DAQ3B: mA: 32
[5 empty] | Xitrons Required |  | Facility Flow Meters
[5 empty] | Unit input (XT-042) |  | COND_SYS01_WTR_E_FLOW_01 (Condenser)
EVAP_SYS01_WTR_E_FLOW_01 (Evaporator)
OIL_SYS01_WTR_CLR-E_FLOW_01 (Aux cooling)
RTD Channels |  | 2024-10-07 |  | TR24-0131 / 450 Ton | WC 500-3 SR
Ref ID | DAQ Driver | Channel | Serial number | Description/Location | LabVIEW Tag Names | Length
WRTD 1 | %DAQ3B_RTD_001% | DAQ3B: RTD: 1 | X | COMPRESSOR SUCTION TEMP | COMPR_SYS01_RFG_SUCT_TEMP_01 | 8"
WRTD 2 | %DAQ3B_RTD_002% | DAQ3B: RTD: 2 | X | COMPRESSOR DISCHARGE TEMP | COMPR_SYS01_RFG_DISCH_TEMP_01 | 8"
WRTD 3 | %DAQ3B_RTD_003% | DAQ3B: RTD: 3 | X | REFRIGERANT LIQUID TEMP TO EXPANSION VALVE #1 | EVAP_SYS01_RLIQ_EV-E_TEMP_01 | 8"
WRTD 4 | %DAQ3B_RTD_004% | DAQ3B: RTD: 4 | X | REFRIGERANT LIQUID TEMP TO EXPANSION VALVE #2 | EVAP_SYS02_RLIQ_EV-E_TEMP_01 | 8"
WRTD 5 | %DAQ3B_RTD_005% | DAQ3B: RTD: 5 | X | OIL COOLER WATER ON | OIL_SYS01_WTR_CLR-E_TEMP_01 | 8"
WRTD 6 | %DAQ3B_RTD_006% | DAQ3B: RTD: 6 | X | OIL COOLER WATER OFF | OIL_SYS01_WTR_CLR-L_TEMP_01 | 8"
WRTD 7 | %DAQ3B_RTD_007% | DAQ3B: RTD: 7 | X | AMBIENT TEMPERATURE | AMB_UNIT_AIR_EXT_TEMP_01 | 10"
WRTD 8 | %DAQ3B_RTD_008% | DAQ3B: RTD: 8 | X |  |  | 10"
WRTD 9 | %DAQ3B_RTD_009% | DAQ3B: RTD: 9 | X |  |  | 10"
WRTD 10 | %DAQ3B_RTD_010% | DAQ3B: RTD: 10 | X |  |  | 10"
WRTD 11 | %DAQ3B_RTD_011% | DAQ3B: RTD: 11 | X |  |  | 10"
WRTD 12 | %DAQ3B_RTD_012% | DAQ3B: RTD: 12 | X |  |  | 10"
WRTD 13 | %DAQ3B_RTD_013% | DAQ3B: RTD: 13 | X |  |  | 10"
WRTD 14 | %DAQ3B_RTD_014% | DAQ3B: RTD: 14 | X |  |  | 10"
WRTD 15 | %DAQ3B_RTD_015% | DAQ3B: RTD: 15 | X |  |  | 12"
WRTD 16 | %DAQ3B_RTD_016% | DAQ3B: RTD: 16 | X |  |  | 12"
WRTD 17 | %DAQ3B_RTD_017% | DAQ3B: RTD: 17 | X |  |  | 8"
WRTD 18 | %DAQ3B_RTD_018% | DAQ3B: RTD: 18 | X |  |  | 8"
WRTD 19 | %DAQ3B_RTD_019% | DAQ3B: RTD: 19 | X |  |  | 8"
WRTD 20 | %DAQ3B_RTD_020% | DAQ3B: RTD: 20 | X |  |  | 8"
WRTD 21 | %DAQ3B_RTD_021% | DAQ3B: RTD: 21 | X |  |  | 8"
WRTD 22 | %DAQ3B_RTD_022% | DAQ3B: RTD: 22 | X |  |  | 8"
WRTD 23 | %DAQ3B_RTD_023% | DAQ3B: RTD: 23 | X |  |  | 10"
WRTD 24 | %DAQ3B_RTD_024% | DAQ3B: RTD: 24 | X |  |  | 10"
WRTD 25 | %DAQ3B_RTD_025% | DAQ3B: RTD: 25 | X |  |  | 10"
WRTD 26 | %DAQ3B_RTD_026% | DAQ3B: RTD: 26 | X |  |  | 10"
WRTD 27 | %DAQ3B_RTD_027% | DAQ3B: RTD: 27 | X |  |  | 10"
WRTD 28 | %DAQ3B_RTD_028% | DAQ3B: RTD: 28 | X |  |  | 10"
WRTD 29 | %DAQ3B_RTD_029% | DAQ3B: RTD: 29 | X |  |  | 10"
WRTD 30 | %DAQ3B_RTD_030% | DAQ3B: RTD: 30 | X |  |  | 10"
WRTD 31 | %DAQ3B_RTD_031% | DAQ3B: RTD: 31 | X |  |  | 12"
WRTD 32 | %DAQ3B_RTD_032% | DAQ3B: RTD: 32 | X |  |  | 12"
TC Channels |  | 2024-10-07 |  | TR24-0131 / 450 Ton | WC 500-3 SR
Ref ID | DAQ Driver | Channel | Serial number | Description/Location | LabVIEW Tag Names | Range
TC 1 | %DAQ3B_TC_001% | DAQ3B TC: 1 | X | OIL ON OIL COOLER | OIL_SYS01_OIL_CLR-E_TEMP_01 | 0-350°F
TC 2 | %DAQ3B_TC_002% | DAQ3B TC: 2 | X | OIL OFF OIL COOLER | OIL_SYS01_OIL_CLR-L_TEMP_01 | 0-350°F
TC 3 | %DAQ3B_TC_003% | DAQ3B TC: 3 | X | OIL SUMP TEMP | OIL_SYS01_SUR_SUMP_TEMP_01 | 0-350°F
TC 4 | %DAQ3B_TC_004% | DAQ3B TC: 4 | X | OIL OFF BEARINGS TEMP | OIL_SYS01_SUR_BRG-L_TEMP_01 | 0-350°F
TC 5 | %DAQ3B_TC_005% | DAQ3B TC: 5 | X |  |  | 0-350°F
TC 6 | %DAQ3B_TC_006% | DAQ3B TC: 6 | X |  |  | 0-350°F
TC 7 | %DAQ3B_TC_007% | DAQ3B TC: 7 | X |  |  | 0-350°F
TC 8 | %DAQ3B_TC_008% | DAQ3B TC: 8 | X |  |  | 0-350°F
TC 9 | %DAQ3B_TC_009% | DAQ3B TC: 9 | X |  |  | 0-350°F
TC 10 | %DAQ3B_TC_010% | DAQ3B TC: 10 | X |  |  | 0-350°F
TC 11 | %DAQ3B_TC_011% | DAQ3B TC: 11 | X |  |  | 0-350°F
TC 12 | %DAQ3B_TC_012% | DAQ3B TC: 12 | X |  |  | 0-350°F
TC 13 | %DAQ3B_TC_013% | DAQ3B TC: 13 | X |  |  | 0-350°F
TC 14 | %DAQ3B_TC_014% | DAQ3B TC: 14 | X |  |  | 0-350°F
TC 15 | %DAQ3B_TC_015% | DAQ3B TC: 15 | X |  |  | 0-350°F
TC 16 | %DAQ3B_TC_016% | DAQ3B TC: 16 | X |  |  | 0-350°F
TC 17 | %DAQ3B_TC_017% | DAQ3B TC: 17 | X |  |  | 0-350°F
TC 18 | %DAQ3B_TC_018% | DAQ3B TC: 18 | X |  |  | 0-350°F
TC 19 | %DAQ3B_TC_019% | DAQ3B TC: 19 | X |  |  | 0-350°F
TC 20 | %DAQ3B_TC_020% | DAQ3B TC: 20 | X |  |  | 0-350°F
TC 21 | %DAQ3B_TC_021% | DAQ3B TC: 21 | X |  |  | 0-350°F
TC 22 | %DAQ3B_TC_022% | DAQ3B TC: 22 | X |  |  | 0-350°F
TC 23 | %DAQ3B_TC_023% | DAQ3B TC: 23 | X |  |  | 0-350°F
TC 24 | %DAQ3B_TC_024% | DAQ3B TC: 24 | X |  |  | 0-350°F
TC 25 | %DAQ3B_TC_025% | DAQ3B TC: 25 | X |  |  | 0-350°F
TC 26 | %DAQ3B_TC_026% | DAQ3B TC: 26 | X |  |  | 0-350°F
TC 27 | %DAQ3B_TC_027% | DAQ3B TC: 27 | X |  |  | 0-350°F
TC 28 | %DAQ3B_TC_028% | DAQ3B TC: 28 | X |  |  | 0-350°F
TC 29 | %DAQ3B_TC_029% | DAQ3B TC: 29 | X |  |  | 0-350°F
TC 30 | %DAQ3B_TC_030% | DAQ3B TC: 30 | X |  |  | 0-350°F
TC 31 | %DAQ3B_TC_031% | DAQ3B TC: 31 | X |  |  | 0-350°F
TC 32 | %DAQ3B_TC_032% | DAQ3B TC: 32 | X |  |  | 0-350°F
Reference ID naming:
P = Pressure Transducer
DP = Differential Pressure
F = Flow Meter
NOTE: DP are pressure differentials. All pressure differentials should be mounted so that the instrument is at the highest point and all lines run continuously down hill to the measurement location with no liquid traps. Keep lines as short as possible.
Reference ID naming:
WRTD = Resistance RTD (0-200°F)
NOTE: RTDs in thermal wells should be installed with a coating of thermal paste.
Reference ID naming:
TC = Thermocouple